## Sheet1
Description | Note | Maintenance frequency | Implementation
Use/adjustment of air compressors' operational order | Turn off/ adjust the operational order of unnecessary air compressors | Daily | Yes
Overall visual inspection | Complete the overall visual inspection to ensure that all equipment are in good working conditions and safety systems are in the right place | Daily | Yes
Quantification of leaks | Detect and report any leaking points in the system | Daily | Yes
Operation of the air compressor | Monitor the compressor during operation and temperature variation from standard curve. | Daily | Yes
Air dryer | Monitor air dryers for proper operation | Daily | Yes
Air compressor ventilation | Make sure that the ventilation system is suitable for the air compressor and air inlet | Daily | Yes
Lubrication of the air compressor | Note the level, color, and pressure. Compare with trend-driven values. | Daily | Yes
Drainage of condensate | Drain the condensate from storage tank, low points and/or filters | Daily | Yes
Operating temperature | Verify that the operating temperature meets the manufacturer's specifications | Daily | Yes
Pressure relief valve | Confirm that all pressure relief valves are in good working condition | Weekly | Yes
Check belt tension | Check that the belt tension and alignment are set correctly | Weekly | Yes
Air inlet filter gasket | Clean or replace the filter gasket as needed | Weekly | Yes
Check pneumatic equipment | All equipment using compressed air should be tested for leaks regularly. Leaks usually occur in: - worn / cracked / frayed nozzles - Clogged air valves - Packed cylinder | Weekly | Yes
Condensate drains | Clean the deposits and check for operation | Weekly | Yes
Motor bearings | Lubricate the motor bearings as recommended by the manufacturer | Monthly | Yes
System oil | Depending on the use and size of the air compressor, take oil samples periodically to monitor moisture, molecular levels and other contaminants. Replace oil if necessary. | Monthly | Yes
Couplings | Check that all couplings are in good working condition and proper alignment | Annually | Yes
Gaskets of the motor shaft | Check all gaskets for leaks or wear and tear | Annually | Yes
Airflow filter | Replace oil and particles removing components when the air pressure drop exceeds 2-3 psid | Annually | Yes
Check the stands | Check and make sure all compressor stands are solid | Annually | Yes